Texas Commission on Environmental Quality

COMPLIANCE AGREEMENT

CITY OF______

Enforcement Case No. 27143

Utilities Registration No. 10060

______County, Texas

The Texas Commission on Environmental Quality ("Commission" or "TCEQ") is the state agency charged with enforcing Tex. Water Code ch. 26 (the "Code") and the regulations promulgated pursuant to the Code.

The City of  _______(Athe City@) owns and operates a wastewater collection system located in ______ County, Texas ("the System").

The City has reported 64 unauthorized discharges totaling 28,670 gallons for Fiscal Year 2004 and 20 unauthorized discharges totaling 9,400 gallons for Fiscal Year 2005.  The majority of these discharges were due to grease blockages. The City will be required to rehabilitate the System to insure a reduction of risk to the public health and the environment, and to comply with Commission requirements.

PROVISIONS

In response to these deficiencies and in an effort to eliminate the potential threat to public health, the City and the Commission have entered into a Compliance Agreement ("CA").  This CA formalizes the commitments made by the City in its letter to the TCEQ dated October 12, 2005 (see Attachment AA@).  The provisions of this CA are as follows:

1.	The City shall replace the existing sanitary sewer lines in targeted neighborhoods with deteriorated infrastructure.  See Attachment AA@ regarding location and the estimated time frames of completion.  Should the City deem it necessary to modify the schedule in Attachment AA@, the City shall notify the Commission in writing at least 30 days prior to making any changes.

2.	The City shall update the Master Sanitary Sewer Plan no later than April 30, 2008, then every five years thereafter.  The plan should include modeling of all sanitary sewer lines ten inches in diameter or greater.  The update should address any existing deficiencies (inadequate capacities) within the collection system as well as future projects to meet development needs.

3.	The City shall update the geographic information systems map for the sanitary sewer collection system to reflect actual location and related information of its sanitary sewer facilities.  This update will occur throughout each year as information becomes available.

4.	The City shall perform an annual inspection of existing manholes.  Maintenance crews will inspect at least 20 percent of the total sanitary sewer manholes within the collection system each year (system total of 4,600 manholes).  Maintenance crews will rehabilitate manholes when necessary during the inspection process.

5.	The City shall clean at least 25 percent of the collection system on an annual basis (system total of 2,500,000 feet).  Maintenance crews will video at least 84,000 feet of the collection system on an annual basis.

6.	The City shall utilize an annual chemical root control program in the collection system where needed.

7.	The City shall introduce an education program to all residential customers for the proper disposal of grease.  Once a year, this information will be included in the Mainstream, the City=s monthly newsletter and the residents= water bill.  This information will be added to the City=s website when developed.  These documents will be printed in both English and Spanish.

8.	Within 90 days of the effective date of this CA, and on an annual basis thereafter, the City shall submit a progress report to the Commission.  These reports shall include information regarding actions taken by the City towards completion of the Provisions of this CA.

9.	By December 31, 2013, the City shall submit in writing certification of compliance with Provision Nos. 1 through 7.

10.	The Executive Director may grant an extension to any provisions of this CA upon a written and substantiated showing of good cause.  All requests for extensions by the City shall be made in writing to the TCEQ.  Extensions are not effective until the City receives written approval from the TCEQ.  The determination of what constitutes good cause rests solely with the TCEQ.

11.	The City shall submit copies of all correspondence, reports, and documentation required by Provision Nos. 1 through 10 to:

Order Compliance Team (MC 149A)

Enforcement Division

Texas Commission on Environmental Quality

P.O. Box 13087

Austin, Texas 78711-3087

with a copy to:

Manager, Water Section

Dallas/Fort Worth Regional Office

Texas Commission on Environmental Quality

2309 Gravel Drive

Dallas/Fort Worth, Texas  76118-6951

In return for the City's agreement and adherence to these terms, the Commission will withhold further enforcement actions related to the noted deficiencies.  Should unforeseen circumstances indicate a need to alter the above mentioned schedule, the utility must immediately notify the Commission so that an amendment can be discussed.

The effective date of this CA is the signature date of the City's authorized representative.  Acceptance of the terms of this CA is indicated by the signatures below.

__________________________________	_____________________	______________

Authorized representative of			Title				Date

City of _________

__________________________________

Printed Name of authorized representative

for City of _______

__________________________________________				_______________

Bryan Sinclair, Manager								Date

Enforcement Section I, Enforcement Division

Instructions: 	Send this signed, original Compliance Agreement to Lynley Doyen, Enforcement Team 1, Enforcement Section I, Enforcement Division, MC 169, Texas Commission on Environmental Quality, P.O. Box 13087, Austin, Texas 78711-3087.