## Slide 1: Environmental Impacts of Corrosion Control Treatment A Case Study in Washington, D.C.
Presented by Laura Dufresne, P.E.
The Cadmus Group, Inc.
NACWA Summer Conference
July 19, 2006
Notes: Steve just discussed the engineering challenges related to the DC lead issue and provided a summary of the many research tools used to find a solution to reduce lead levels. I’m going to focus on one research study done in the spring of 2004, prior to the start of the new treatment, to screen for any potential negative environmental effects.

## Slide 2: Acknowledgments
This paper was prepared with assistance from:
Rich Giani, DCWASA Shari Ring, The Cadmus Group, Inc.
Jennie Saxe, EPA Region 3 Stephanie Jones, The Cadmus Group, Inc.
Key contributors to the study include but are not limited to:
Rick Rogers, EPA Region III
George Rizzo, EPA Region III
Gary Miller, EPA Region III
Mary Letzkus, EPA Region III
Jonathan Essoka, EPA Region III
Vicky Binetti, EPA Region III
Dave Hundelt, Arlington County
Larry Slattery, Arlington County
Robert Etres, City of Falls Church
Aklile Tesfaye, DCWASA
Walt Bailey, DCWASA
Nicolette Shulterbrant, DCDOH
Dr. Charles Bott, Virginia Military Institute
Hawaii Department of Health
Illinois Environmental Protection Agency
Massachusetts Department of Environmental Protection
Missouri Department of Natural Resources
New York State Department of Health
Wisconsin Department of Natural Resources

## Slide 3: Overview
The Treatment Decision
The Study Methodology
State Experience
Pathways from the Distribution System to Receiving Stream
Increased Chemical Loads to Receiving Waters
Wastewater Treatment Impacts
Additional Research

## Slide 4: The Treatment Decision
April 8, 2004: The Washington Aqueduct recommends orthophosphate.
April 15, 2004: Outside panel of experts recommends zinc orthophosphate because of its success at other large utilities.
Recommendation was adopted:
  Zinc PO4 Dose = average of 3 mg/L as PO4 at customer tap
  PO4 to Zinc Ratio = 10:1
  Zinc concentration at tap ~ 0.3 mg/L
  Reduce to a “maintenance” dose of 1 mg/L as PO4 after 6 mo - 1 yr
Notes: Rich and Jennie – can you double check the dates?

## Slide 5: The Environmental Impacts Study
In April 2004, EPA commissioned a study to screen for potential negative impacts of adding zinc orthophosphate to the drinking water. Full report is available on-line at http://www.epa.gov/dclead/Impacts_report_final.pdf
Found 3 potential impacts (all 3 related to zinc)
  Exceed TMDLs for zinc
  Endangered species in Rock Creek sensitive to zinc
  Potential to inhibit nitrification process at Arlington WPCP*
Notes: This was a SCREENING analysis to identify potential negative impacts.
Quick turnaround study with majority of work completed within 2 months
Used conservative assumptions to make assessments to identify potential problems.
Note that I’m not going to cover each analysis in detail but hit the high points with this presentation. Detail is available in on-line report.

## Slide 6: Revised Treatment Decision
May 27, 2004: As a result of the Environmental Impacts Study, changed back to orthophosphate.
Orthophosphate
(PO4)
Zinc
Orthophosphate
(ZnOP)
Notes: Came full circle
Started with orthophosphate, changed to zinc orthophosphate based on recommendations from peer review panel, then changed back to orthophosphate because of this environmental impacts study. Key driver was WWTP, although study identified three potential negative impacts of zinc.

## Slide 7: The Study Methodology
Contacted States
Collected Data
  Identify and characterize impacted waters
  Review local standards and regulations, including water quality criteria, TMDLs, Storm Water permits, and NPDES Permits
  Research sensitive species
  Identify receiving WWTP and characterize treatment.
Conducted Screening Analyses
  Assuming worst-case conditions
  Goal was to identify potential problems
Notes: Performed extensive web research, database searches, on-site interviews

## Slide 8: The Study Methodology (cont.)
Performed by multi-disciplinary team of EPA and consultant personnel:
Environmental engineering
Environmental science
Wastewater treatment
Water resources
Toxicology
Pretreatment and TMDL program experience

## Slide 9: State Experience With Corrosion Inhibitors
Targeted states with large number of lead service lines
6 states contacted
Notes: Hawaii was also selected because of a reported possible link between skin and eye irritations and use of zinc orthophosphate.
Question for Rich and Jennie: What is the status of the Hawaii situation?
We asked states about:
- prevalence of phosphate-based corrosion inhibitors
- primary form (zinc / ortho / blend)
- any known cases of detrimental environmental impacts
- would the state generally approve the dosing strategy for D.C.

## Slide 10: State Experience With Corrosion Inhibitors
Phosphate-based corrosion inhibitors used in 5 of 6 states
Practices vary among states
2 systems in New York and 1 in Wisconsin did not use phosphate-based corrosion inhibitors due to discharge concerns
  Algae growth in finished water reservoirs
  High phosphate discharge to receiving streams
No reported problems with zinc
Notes: Missouri reported that their waters had high enough alkalinity and pH to precipitate calcium carbonate for corrosion control.
Some states prefer zinc orthophosphate, others tended to favor orthophosphate or polyphosphate blends.
Few reported environmental problems with phosphate-based corrosion inhibitors with a few exceptions.

## Slide 11: Where Does the Water Go?
When water leaves the distribution system, it usually makes it way into local receiving streams.
Some is treated at WWTPs.
Some is discharged directly without treatment.
Notes: Discharged water can also make its way into ground water or be evaporated, but most makes its way to area receiving streams.

## Slide 12: Area Served by D.C. Water
Notes: To identify the major pathways from distribution system to receiving stream, we first need to identify the WA service area. Washington Aqueduct water is sold not only to D.C., but also to arlington county and falls church in VA. It is not possible to delineate between the systems, so any chemical added to D.C. water is also added to water delivered to Arlington and Falls Church.

## Slide 13: Where Does the Water Go? (cont.)
Notes: Here is a diagram showing the various pathways from the three distribution systems to receiving streams. Couple of interesting things to note:
About 1/3 of DCWASA’s system is a combined sewer system. This means that during heavy rainfall events, water from the combined system is discharged directly to receiving waters rather than making its way to the treatment plant.
Average flow of the Arlington plant is 30 MGD, but peak stormwater flow has been as high as 130 MGD. The main reason for this is pre-1968 plumbing code allowing foundation drains to be directly connected to sanitary sewer systems. When the hydraulic capacity of the plant is exceeded, partially treated wastewater is discharged directly to Four Mile Run. County is in the process of installing equalization tanks and has plans to eliminate all bypasses by 2012.

## Slide 14: Potential Impact of Potable Water Discharges on Receiving Streams
Screening Analysis Methodology
Quantify increased zinc and phosphorus load (conservative assumptions)
Compare to water quality criteria, background levels, and TMDLs (where applicable)
Search for species sensitive to zinc, estimate impact for worst case scenario
Notes: These are the discharges from the previous slide that are not treated at area WWTPs

## Slide 15: Quantify Increased Loads to Receiving Waters
Contributions from
  Potable water discharges
    Utility discharges (e.g., flushing, breaks)
    Customer activities (e.g., lawn watering, car washing)
  CSO discharges (D.C. only)
  WWTP bypasses (Arlington only)
Notes: [add background picture of hydrant discharge]
First two categories are common to almost all localities. Utilities often flush in response to deteriorating WW or complaints. Many cities also have dedicated program to flush a certain percentage of the distribution system each year. Currently, frequency of flushing in D.C. is based on water quality monitoring. If data from an area show decreased chlorine residual, increased bacteria counts, or other trigger, then the area is flushed more frequently. Arlington typically flushes their system in the spring time.
In addition to planned discharged initiated by the utility, all water systems experience some frequency of unplanned discharges. These are things like water main breaks, blown hydrants, etc.
Discuss customer activities: most would infiltrate into ground water
At that time, no available estimates of volume for utility discharges
Focused on
- CSO discharges
- Plant bypasses

## Slide 16: Contribution from CSO Discharges
1/3 of DC system is combined (most constructed before 1900)
60 total CSO outfalls to Rock Creek, Anacostia River, and the Potomac River
Data on discharge frequency and volume available in DCWASA’s LTCP (2002)
EPA and DCWASA experts estimate that 25% - 33% of CSO discharges are domestic wastewater
CSO discharges will decrease significantly in future years
Notes: Most of combined area was constructed pre-1900
We used data from WASA’s Combined Sewer System Long Term Control Plan (2002) to estimate total volume discharged per year. Combined with expert estimates of the proportion of CSO discharges that are domestic WW
To calculate the total volume of domestic water discharged through CSO’s,

## Slide 17: Contribution from WWTP Bypasses
Arlington estimates that:
An average of 8 bypass events occur per year
Average volume ~ 10 MG
Approximately 1/3 is domestic wastewater
All bypasses will be eliminated by 2012
Notes: Picture to be added

## Slide 18: Compare to Regulations and Standards
Water Quality Criteria
Storm water discharge permits
TMDLs
Endangered species
Phosphorous loading to the Chesapeake Bay
Notes: Picture to be added

## Slide 19: Finding #1: TMDL for Zinc
Stream | TMDL for Zinc (lb/year) | Estimated increased zinc from CSO discharge (lb/year) | Percentage increase
Rock Creek | 691 | 13 – 27 | 2 – 4%
Anacostia (& tributaries) | 6,615 | 351 – 706 | 5 – 11% *
*Identified as a potential problem in screening analysis |  |  | 

## Slide 20: Finding #2: Endangered Species in Rock Creek Sensitive to Zinc
Hay’s Spring Amphipod found in only 2 locations in Rock Creek
Acute toxicity for zinc = 0.315 mg/L at hardness of 100 mg/L CaCO3. This is still higher than the WQC of 0.106 mg/L
Background Zinc in Rock Creek Typically 0.02 – 0.08 mg/L
The Hay’s Spring Amphipod is a federally listed endangered species living in Rock Creek

## Slide 21: Finding #2: Endangered Species in Rock Creek Sensitive to Zinc (cont.)
CSO discharges evaluated, not a problem because of diluted zinc concentration
Hypothetical large water main break discharging into Rock Creek
  Assumptions
  Zinc concentration in distribution system = 0.5 mg/L
  Minimum stream flow, high discharge flow
  Finding
  Could temporarily exceed WQC of 0.106 mg/L and approach toxic concentration for Hay’s Spring Amphipod
  Identified as potential problem in screening analysis
  True impacts expected to be minimal because of dilution (125 feet mixing zone)

## Slide 22: Phosphorous in discharge water not expected to permanently change phosphorous (P) level in receiving streams. Increased P Load to Chesapeake Bay expected to be minimal compared to total load
Current P Load (lbs/year)* | Increase from CSO, Bypass | % of Total**
18.8 million | 1,865 – 3,763 | 0.01 – 0.02 %
* P load goal for 2010: 12.8 million lbs/year. ** % increase considering P load goal for 2010: 0.015 – 0.03 % |  | 
Other Findings

## Slide 23: Potential Impacts on Area Waste Water Treatment Plants
Two plants Identified:
Blue Plains Advanced Waste Water Treatment Plant (AWTP)
  Largest plant of its type in U.S.
    rated flow of 370 MGD
    peak wet weather capacity of 1 BGD
  45% flow from DC, 45 % from MD, 10 % from VA
  Discharges to Potomac River
  Biosolids are land-applied
Notes: Mention that Blue Plains has nitrification / denitrification as well and filtration treatment capabilities
Arial photo is from WASA’s website showing planned egg shape digesters

## Slide 24: Potential Impacts on Area Waste Water Treatment Plants (cont.)
2) Arlington Water Pollution Control Plant
  Advanced waste water treatment plant
  Rated capacity of 40 MGD except biological nutrient removal process (30 MGD)
  Nearly all influent flow from Arlington county
  Discharges to Four Mile Run
  Biosolids are land-applied
Notes: Mention that Blue Plains has nitrification / denitrification as well and filtration treatment capabilities

## Slide 25: Impacts of Increased Phosphorous Load
Both plants add Ferric Chloride to remove Phosphorous
Increased influent Phosphorous means increased costs for
  Higher Ferric Chloride dose
  Increased sludge production
Cost analysis found that
  for Blue Plains, additional $ is < 0.5% of annual operating budget
  for Arlington, additional $ is < 0.6% of annual operating budget
Concluded that additional phosphorous would not adversely impact plant operations.
Notes: Not shown here, but we also evaluated impacts of changes in pH

## Slide 26: Impacts of Increased Zinc Load
First Concern: Allowable zinc concentration in land applied sludge (permitted)
  Permitted allowable = 2,500 mg/kg sludge
  Measured zinc for Blue Plains ~ 280 mg/kg
  Measured zinc for Arlington 200 – 300 mg/kg
Both plants are well below limits. Increased zinc in sludge not expected to have significant impact on land application of sludge

## Slide 27: Impacts of Increased Zinc Load
  Second Concern: Inhibitory effects on biological removal processes
    Activated sludge
    Nitrification process –
    most sensitive
    EPA has general guidelines, but inhibition is site-specific
Arlington most at risk because all domestic influent water will have higher zinc (at Blue plains, only 45% of water will have increase zinc concentration)
Notes: Add picture of nitrification bacteria under microscope?

## Slide 28: Inhibitory Limits of Zinc to Activated Sludge and Nitrification
 | Inhibitory Limit (mg/L) | Reference
Activated Sludge | 0.3 – 5 | (Anthony, R.M. and L.H. Briemburst, 1981) Cited in EPA Guidance
 | 5 – 10 | (Jenkins, D.I. and Associates, 1984) Cited in EPA Guidance
 | 0.3 | (Juliastuti, S.R. et al., 2003)
 | 0.57 – 10 | (Madoni et al., 1996)
 | 30 (total), 7.6 (dissolved) | (Sharma et al., 2001)
Nitrification | 0.08 – 0.5 | (Russell, L.L., et al., 1984) (Anthony, R.M. and L.H. Briemburst, 1981) Cited in EPA Guidance
 | 0.08 – 1.2 | (Juliastuti, S.R. et al, 2003) 12% - 100% inhibition
 | 0.08 – 0.5 | (Eysenback, 1994)

## Slide 29: Impacts of Increased Zinc Load
Wastewater Treatment Plant | Average Influent zinc concentration (mg/L) | increase in influent Zinc (mg/L)* | New Influent Zinc Concentration (mg/L)
Blue Plains | 0.06 | < 0.14 | < 0.2
Arlington | 0.18 | 0.3 | 0.48
*Based on initial zinc orthophosphate dose of 3 mg/L as PO4, 10:1 phosphate to zinc ratio.
Finding #3, Potential Problem for Arlington – near high end of EPA-published zinc inhibitory limit, concern about upsetting nitrogen removal process.

## Slide 30: Treatment Change
In May of 2004, Technical Expert Working Group switches back to orthophosphate
Even the best intentions can be misinterpreted
…[C]ouncil member Carol Schwartz (R-At Large) said that she was uneasy about the sudden switch and that “I need a comfort level here.” When she learned that the new chemical would cost 30% less than the old one, she demanded reassurance that money was not the motivation.
Washington Post, May 27, 2004

## Slide 31: Additional Research
In June 2005, initiated new on-site study at Arlington WPCP to determine if 0.5 mg/L influent zinc would inhibit nitrification.
Why? In case the orthophosphate is not working as quickly or as well as expected
Jointly funded by EPA Region 3 and Arlington County
Conducted by Dr. Charles Bott from Virginia Military Institute

## Slide 32: Additional Research (cont.)
Approach
Hypothesized that 0.5 mg/L of zinc would have no inhibitory effects. Tested hypothesis under worst case conditions
Methods for Quantifying Inhibition
  Respirometry
  Nitrate/Nitrite Generation Rate Measurements
Results
  Observed rapid inhibition at high zinc levels (10 - 50 mg/L), but no inhibition at 0.5 mg/L under ultra-sensitive conditions
  Predicted zinc inhibitory effect at approximately 1.0 mg/L
Notes: Worst case conditions of experiment:
- used stock solution of soluble zinc (?), not premixed in wastewater
- did not consider any zinc removal in primary clarifying
- no prior acclimation of nitrifying bacteria to zinc

## Slide 33: For More Information:
www.dcwasa.com
www.epa.gov/dclead
Contact me at ldufresne@cadmusgroup.com
For more information on the research at Arlington WPCP, contact Dr. Bott at bottCB@vmi.edu
Questions?
DISCLAIMER: Any opinions expressed in this paper are those of the author(s) and do not, necessarily, reflect the official positions and policies of the USEPA. Any mention of products or trade names does not constitute recommendation for use by the USEPA. Existing data from sources within or outside of the USEPA for informational purposes were not subjected to the USEPA’s quality assurance procedures and there was no attempt to verify the quality of the data collected from the various sources.