## Slide 1: DC WASA Lead Issues and SDWA Simultaneous Compliance
Engineering CHALLENGES
Engineering SOLUTIONS
Steve Reiber, CH2M HILL
Rich Giani, DC WASA
July, 2006

## Slide 2: Purpose of this Presentation:
to define the complexity of the problem and recognize the engineering research that identified a compatible system-wide mitigation strategy.
<number>

## Slide 3: Acknowledgments
Laura Dufresne, The CADMUS Group
Greg Kirmeyer, HDR Engineering
John Wujek, Hatch Mott MacDonald
John Civardi, Hatch Mott MacDonald
Gregory Korshin, University of Washington
Mike Schock, EPA Office of Research and Development
This paper was prepared with substantial contributions from:
<number>

## Slide 4: The DC Lead experience has helped change corrosion science (as regards distribution systems) in several meaningful ways:
Issues of magnitude
Interactions of materials
Questions of measurement
Corrosion Indices
Redox stability of corrosion scales
<number>

## Slide 5
The District of Columbia Water and Sewer Authority (DC WASA) is just one entity in a consecutive system supplied treated water from the Potomac by the U.S. Army Corps of Engineers (Aqueduct Authority).
<number>

## Slide 6: To ensure compliance with Stage II of the DBP Rule, the Aqueduct converted to chloramination (2001).
1990
2000
Free Chlorination
Chloramination
NH2Cl
Secondary Disinfectant
No good deed goes unpunished. Chloramination was an appropriate response to a public health issue (DBPs). There was little (none) case-history literature to suggest the importance of lead-oxide re-equilibration.
<number>

## Slide 7: Redox potential influences the mineral forms of oxidized lead.
Free chlorine conditions
Chloramine conditions
Pb(II) mineral solubility >> Pb(IV) mineral oxides
<number>

## Slide 8: The engineering challenges were many and varied, but generally fell into one of seven categories.
<number>

## Slide 9
Challenge: Identify the source and nature of the metals release!
Household Lead Profile
LCR Compliance Data
Chloramination implemented
<number>

## Slide 10: Background: How Lead Gets into Drinking Water
The Washington Aqueduct and WASA are responsible for making sure that the water meets federal standards.
<number>

## Slide 11
Challenge: Identify optimal corrosion control strategies!
Multiple and redundant control studies
DC WASA is a consecutive system.
<number>

## Slide 12
Challenge: Implement and monitor mitigation strategy!
Requires an exceptional level of customer participation.
<number>

## Slide 13
Challenge: Maintain distributed water quality during implementation!
Three separate full-time flushing crews operating in the District
Extensive coliform, HPC, turbidity and aesthetic water quality monitoring.
<number>

## Slide 14
Challenge: Identify potential Impacts to wastewater collection and treatment system!
Corrosion inhibitor impact on WWTP nitrification
Discharge limitation for phosphate
Biosolids metals accumulations
<number>

## Slide 15
Challenge: Assessment of on-going Lead Service Line replacement program!
homeowner cooperation
partial replacement
An abundance of LSLs (>28,000) exist in the District.
<number>

## Slide 16
Challenge: On-going simultaneous compliance management / research!
Microbial Quality
  Total Coliform Rule
  Nitrification
Disinfection Byproducts
  THM / HAA formation
  Enhanced coagulation
  NOM management
Corrosion Control
  LCR
  Red Water
<number>

## Slide 17: The solutions to these challenges proceeded on a broad front.
<number>
Notes: <number>
<footer>
<header>
<date/time>
Good to leave some helpful information on the screen as a last slide.

## Slide 18: Solution: The Technical Expert Working Group
Formed in early 2004
Cooperative effort among:
  DC WASA
  Washington Aqueduct
  EPA
  DC Department of Health
  CDC
  Arlington County DPW
  Falls Church DES
  outside consultants
Charge:
  Coordinate ongoing research efforts
  Develop a strategy to reduce lead in drinking water
<number>

## Slide 19: Solution: redundant pilot and bench-scale studies all identify orthophosphate as an effective LSL passivating agent.
Orthophosphate reduced lead leaching in three separate loop studies.
10 mg/L Orthophosphate
No treatment
<number>

## Slide 20: Solution: Orthophosphate Treatment Implementation
Provided by Rich Giani, DC WASA
Over 7 months, 90th percentile lead levels decreased from over 100 ppb to under 15 ppb.
Partial system test followed by full-scale implementation.
Phosphate addition
Action Level
<number>

## Slide 21: Solution: Extensive system monitoring – including household lead profiles
Suspected that lead in water was coming from lead service lines, but could be coming from leaded brass fixtures, lead solder, etc.
WASA conducted Lead Profiling of homes with lead service lines, going well beyond any EPA requirement.
<number>
Notes: <number>
<footer>
<header>
<date/time>
Good to leave some helpful information on the screen as a last slide.

## Slide 22: Typical DC WASA residential lead profile following implementation of the orthophosphate inhibitor program
<number>
Notes: <number>
<footer>
<header>
<date/time>
Good to leave some helpful information on the screen as a last slide.

## Slide 23
Solution: Improved understanding of lead chemistry and mineralogy helps explain the success of the mitigation program.
Findings: Although Pb(II) compounds were thought to be controlling, the scale in the DC WASA system was a mix of both Pb(II) and Pb(IV) scales.
Hydrocerussite
PbO Massicot
PbO Litharge
<number>

## Slide 24: Solution: The most extensive service-line replacement program ever conducted
More than 2000 replacements per year at a cost exceeding $8 million
<number>
Notes: <number>
<footer>
<header>
<date/time>
Font coordination, add bullet and modify note 1.

## Slide 25: Lessons Learned
Conventional LCR monitoring may not be adequate to define all metal release scenarios. Nonetheless, it remains a viable and useful corrosion-control tool.
The chemistry of lead solubility, oxidation and mobility is more complicated than previously understood.
The lead issues are tractable – phosphates are highly effective at passivating LSL surfaces in a chloraminated environment.
<number>

## Slide 26: Lessons Learned
Distribution system re-equilibration is always an issue.
Lead release dynamics can be accurately assessed at the laboratory scale.
Microbial regrowth in the distribution system is a manageable concern – even in the presence of the orthophosphate inhibitor.
<number>

## Slide 27: Lessons Learned
pH control and/or calcite deposition, as corrosion-control strategies, are not sufficiently rigorous for LSLs.
Issues associated with partial LSL replacement are manageable.
<number>

## Slide 28: Continuing Research
Continuing studies using recirculation pipe loops
New studies to evaluate:
  Impact of galvanic corrosion on lead release
  pH management strategies
  Comparison of orthophosphate and zinc orthophosphate
  NOM effects
Additional LSL scale work using X-ray diffraction, Raman-Spectroscopy
New flow-through pipe loop studies to refine treatment
<number>