## Slide 1: Phoenix/SROG Local Limits Evaluation Utilizing EPA Local Limits Development Guidance
Presented by
Henry Day
City of Phoenix
Co-author – Sinziana Vera-Urban, Malcolm Pirnie, Inc.
GLEND LE
2004 National Pretreatment Coordinators Workshop, October 28, 2004, Norfolk, Virginia

## Slide 2: Comments on Use Of EPA Local Limits Development Guidance
General comments
  New guidance is better organized and easier to read
  Good introductions and summaries
  More tables and highlighted equations
  More explicitly describes methodology while allowing flexibility
  Is not very helpful in describing control methods other than numeric limits (BMP’s addressed briefly in Section 6.6)

## Slide 3: Comments on Use Of EPA Local Limits Development Guidance
Disclaimer – The discussion in this document is intended solely as guidance. This guidance is not a regulation nor does it substitute for any requirements under the CWA or EPA’s regulations.
  Intent of the Guidance is to be helpful, non-threatening
  The Guidance suggests possible flexibility in some areas (common sense assessment) – but retains all statutory and regulatory requirements
  While intended solely as guidance, the document is likely to be viewed as the ‘gold standard’ when local limits changes are reviewed by approval authorities

## Slide 4
National Pretreatment Program’s
Three Pollution Control Strategies
National Categorical Discharge Standards
Developed by USEPA
Applied to industries nationally
Numeric criteria
Prohibited Discharge
Standards
Developed by USEPA
Applied to all non- domestic users
General/specific prohibitions
Local
Limits
Developed by local POTWs
Applied to local industries and other users
Site-specific

## Slide 5: Pretreatment Program Mission: Avoid Adverse Effects of Industrial Discharges
Significant Industrial Users (SIUs)
  Protect worker health and safety
  Comply with regulations
Publicly Owned
Treatment Works
(POTW)
Effluent
Biosolids
Residential Users
Commercial users
  Protect effluent quality/end uses
  Protect POTW processes

## Slide 6: Phoenix/SROG Local Limits Studies
First Local Limits Study completed in 1992
Prior to 1992, used 10 times the drinking water limits
1996 Local Limits Update – no changes
Phase I and Phase II Local Limits Update completed in May 2004 and Ordinance modification planned for January 2005

## Slide 7: Phase I Study (2000-2002)
Why do the new study?
  Changes in the system
    Service area & industrial growth
    Addition of water reclamation plants (WRPs)
    WWTP processes
  Changes in criteria
    New APP and NPDES permits
    New surface water quality standards
Goal: Apply the USEPA Screening Criteria (Guidance Section 3.3 – 3.4) and identify the pollutants of concern for 91st Avenue and 23rd Avenue WWTPs

## Slide 8: Pollutants of Concern 91st Avenue and 23rd Avenue
Pollutants that met EPA screening and have current 12
local limits
Pollutants that met EPA screening and are currently 2
prohibited
Pollutants that met EPA screening with no current 8 local limits or prohibition
Pollutants considered special cases 5
Pollutants with existing limits, but did not meet EPA 12 screening
Other pollutants required to be evaluated by EPA 2001 3 Draft Local Limits Guidance
Total 42

## Slide 9: SROG Collection System
Notes: Emphasize 91st and 23rd Avenue WWTP and valley wide limits approach.
Account for deduction of 23rd Avenue WAS sludge, addition of WRP sludge discharges, and configuration of the collection system.
Evaluation of individual WRPs is being done by each City as they see the need.

## Slide 10: 91st Avenue WWTP
  Secondary treatment nitrification/denitrification process
  Effluent – direct use by the Arizona Nuclear Power Plant and
  discharge to Salt River
  Biosolids - Land application
  179 mgd facility
  ~ 5.6% flow is industrial

## Slide 11: 23rd Avenue WWTP
  Tertiary treatment nitrification/denitrification process
  Effluent - irrigation of non-food crops and discharge to Salt
  River
  Biosolids - Land application
  61 mgd facility
  ~ 9.2% flow is industrial

## Slide 12: Comments on Use Of EPA Local Limits Development Guidance
National POC’s (Sections 3.1, 5.3)
  10 pollutants first identified in 1987 Guidance
  Adds molybdenum, selenium – Federal biosolids regulations
  Conventional pollutants – BOD, TSS, ammonia
    Concentrated conventional pollutants from industrial/commercial sources are the primary concern
    Guidance does not provide clear direction for setting numeric limits for conventional pollutants
    Plant design capacity may be best handled through other local studies – (metering and strength study)

## Slide 13: Comments on Use Of EPA Local Limits Development Guidance
Resource Protection Criteria (3.2.5 and 5.2.2)
  Recommends considering aquifer protection permit limits in determining POC’s
  Responsive to issues in the arid southwest

## Slide 14: Phase II Study – Major Tasks
Data analysis
  Review flows and concentration data from January 2000 to December 2002.
  Determine pollutant loadings for each sector
MAHL determination
  Calculate upper limit of pollutant loading that WWTPs can accept with minimal risk of pass-through or interference.
Develop industrial control strategies
Propose limits

## Slide 15: Comments on Use Of EPA Local Limits Development Guidance
Data Needed To Develop Local Limits (Chapter 4)
  Improves and expands discussion of data needs
  Addresses sampling at the POTW, in the collection system, and at industrial users
  Specifically identifies pollutants to be sampled
  Makes distinctions in sampling frequencies for different stages of program development
  Discusses sampling methods and gives examples
  Discusses analytical methods, data management, and review of results

## Slide 16: Comments on Use Of EPA Local Limits Development Guidance
Calculation of Maximum Allowable Headworks Loading (Chapter 5)
  Improves and expands discussions of calculations
  Addresses different methods of calculating removal efficiencies and gives guidance on selecting appropriate method
  Discusses data quality
  Expands discussion of biosolids quality criteria and inhibition criteria
  Discusses FOG

## Slide 17: Maximum Allowable Headworks Loading (MAHL) Determination
Pass-through
  NPDES criteria
  AZPDES criteria
  APP criteria
  AZ SWQS
  AZ AWQS
Effluent
Interference
  Activated Sludge
  Nitrification
  Anaerobic Digestion
Biological
processes
  Federal 503 criteria
  AZ criteria
Biosolids

## Slide 18: Calculate Removal Efficiencies
Influent
Load
Primary
Sediment- ation
Secondary
Treatment
Secondary
Sediment- ation
Disinfection
Anaerobic
Digestion
Biosolids
Primary
Effluent
Primary Sludge Removal
Efficiency
Final Effluent
Overall Removal Efficiency
Primary Sludge
Primary Removal
Efficiency
Secondary Sludge
Issues:
Non-detected results
Wet-stream detention
time

## Slide 19: MAHL Determination
Projected Plant Flow
WWTP Process
Removal Efficiency
MAHL
AHL =_Criteria x Plant Flow__
(1 - Removal Efficiency)
Criteria
Allowable Industrial
Loading
Safety Allowance:
10% for 91st Avenue WWTP
10% - 13% for 23rd Avenue WWTP
Slug loadings
Industrial growth
Background Loading
Domestic
Commercial
WRP Residuals

## Slide 20: Example: MAHL Determination for Lead
Biosolids
Nitrification Inhibition
Activated Sludge Inhibition
AWQS
SWQS
APP
NPDES
Calculated AHLs (lb/d) for Various Criteria
MAHL
Most Stringent
AHL
MAHL protects the most sensitive use
AHL =_Criteria x Plant Flow__
(1 - Removal Efficiency)
Removal Efficiency = 89%
Plant Flow = 48.6 mgd

## Slide 21
UCL method defines one concentration for every industry:
Safety
Allowance
Background
Loadings
(BL)
Allowable
Industrial Loading
(AIL)
Safety
Allowance
(SA)
UCL = __AIL___
Q SIUs
Where:
Q = Flow
AIL = MAHL - SA - BL
Uniform Concentration Limit (UCL)

## Slide 22: Industrial Control Strategy Development
Criteria for Evaluation of Setting/Removing Limit
  Did pollutant meet USEPA screening?
  Have there been WWTP effluent violations?
  Is average influent loading > 60% MAHL or maximum influent loading > 80% MAHL?
MTBE
Benzene
TCE
Total
Chromium
Chloroform
Nickel
Boron
PCE
√
-
0%
0%
2%
6%
9%
41%
13%
-
0%
6%
6%
1%
19%
38%
3%
Do not calculate local limit.
Influent loading to MAHL - 91st Ave WWTP
Influent loading to MAHL - 23rd Ave WWTP
Is maximum daily influent loading > 80% of the
MAHL at either WWTP?
Criteria
Are industrial levels greater than background?
Did pollutant meet USEPA screening?
Have there been effluent violations at WWTPs?
Did not meet EPA Screening
Recommendation
Is there an existing daily average local limit?
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√

## Slide 23: Industrial Control Strategy Development
Criteria for Evaluation of Setting/Removing Limit
√
√
√
√
√
√
-
0%
6%
2%
0.1%
9%
18%
36%
1%
24%
31%
6%
-
0%
7%
6%
2%
7%
25%
34%
24%
41%
40%
35%
Do not calculate local limit
Calculate local limit.
Evaluate BMP implementation.
Are industrial levels greater than
background?
Did pollutant meet USEPA screening?
Have there been effluent violations
at WWTPs?
Recommendation
Is there an existing local limit?
Influent loading to MAHL - 91st
Ave WWTP
Influent loading to MAHL - 23rd
Ave WWTP
Is maximum daily influent loading >
80% of the MAHL at either WWTP?
Criteria
Average Influent / MAHL between 0% and 60% for both WWTPs
2,4-D
CldiBr
MeCl2
Silver
Beryllium
Cadmium
Arsenic
Fluoride
Lead
Zinc
Copper
Cyanide
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√
√

## Slide 24: Industrial Control Strategy Development
Criteria for Evaluation of Setting/Removing Limit
Sulfides
Mercury
Molybdenum
DEHP
Selenium
√
√
√
√
√
√
√
√
√
√
24%
13%
31%
87%
76%
99%
63%
65%
17%
68%
√
√
√
√
√
√
√
√
√
√
Average Influent / MAHL > 60% at
either WWTP
Influent loading to MAHL - 91st Ave WWTP
Influent loading to MAHL - 23rd Ave WWTP
Is maximum daily influent loading > 80% of the
MAHL at either WWTP?
Is there any extenuating circumstances?
Is there any detection limit issue?
Criteria
Are industrial levels greater than background?
Did pollutant meet USEPA screening?
Have there been effluent violations at WWTPs?
Evaluation and Recommendation
Is there an existing daily average limit?
√
√
√
√
√
√
√
√
√
√
√
√
√
√
Calculate local limit.
Evaluate BMP implementation.
Are best management practices (BMPs) applicable?
√
√

## Slide 25
Investigation of Other Pollutants
  Pollutants with fume toxicity hazards
  Compare current pollutant concentrations to screening levels based on chronic and acute exposure limits.
  Set instantaneous limit to protect worker health and safety.
  Prohibited pollutants
  Evaluate collection system and WWTP concentrations.
  Set prohibition to protect end uses.

## Slide 26
Investigation of Other Pollutants (Cont.)
  Total Petroleum Hydrocarbons (TPH)
  Confirm test method variability.
  Evaluate technical validity of 100 mg/L TPH limit for permitted industries.
  Assess inspections and monitoring of BMPs in place of limit.
  Conventional pollutants
  Compare current WWTP influent loading to WWTP design parameters.
  Assess if local limit is necessary to protect effluent water quality.

## Slide 27: Proposed Control Strategies
Recommendation | Pollutant
Update current local limit | Arsenic, copper, lead, mercury, silver, zinc, benzene, and chloroform
Maintain current local limit | Cadmium, cyanide, and selenium
Remove local limit | Boron, chromium, nickel, total sulfides, TPH, CN amenable to chlorination, dissolved sulfides, methylene chloride, tetrachloroethylene, and trichloroethylene
Develop BMP approach | Beryllium, fluoride, molybdenum, selenium, and DEHP
Set new prohibition | 4,4’-DDE, 4,4’-DDT, and aldrin
Maintain current prohibition | BHC-alpha, BHC-beta, BHC-gamma, heptachlor, heptachlor hepoxide, and PCBs
Remove current prohibition | Chrysene and phenanthrene

## Slide 28: Comments on Use Of EPA Local Limits Development Guidance
Determination of Need For Local Limits (6.1.1)
  Comparison of influent loading to MAHL provides a practical and useful methodology to establish the need for a local limit, or to maintaining existing limits.

## Slide 29: Comments on Use Of EPA Local Limits Development Guidance
Common Sense Assessment (Section 6.5)
  Are the limits technologically achievable?
    Is treatment technology available? Are there alternatives?
  Can the POTW and dischargers determine compliance with the local limits?
    Are the limits above sampling method detection levels?
  Are the limits sensible in light of actual conditions at the treatment plant and past compliance experience?
    This area is subjective and case-specific

## Slide 30: Are there other options? BMPs and Public Education
Treatment technology may be limited
Non-industrial sources are significant contributors
Only certain specific types of industries are the contributors
Pollution prevention may be more effective

## Slide 31
Current Activities
  Implementation of Ordinance modification
    End of Public period in August 2004
    Submittal of Industrial Pretreatment Program modification to ADEQ in mid October 2004
  Development of BMP approach for 5 pollutants: beryllium, fluoride, molybdenum, selenium, and DEHP

## Slide 32
National Pretreatment Program’s
Three Pollution Control Strategies
National Categorical Discharge Standards
Developed by USEPA
Applied to industries nationally
Numeric criteria
Prohibited Discharge
Standards
Developed by USEPA
Applied to all non- domestic users
General/specific prohibitions
Local
Limits
Developed by local POTWs
Applied to local industries and other users
Site-specific
In some cases, the use of best management practices (BMPs) may be preferred over local limits

## Slide 33: Best Management Practices (BMPs)
BMPs are, for example, schedules of activities, practices or devices that are the most effective and practical means to prevent or reduce the amount of pollutants entering the sanitary sewer system, surface water, air, land or groundwater.
BMPs may include any type of pollution control measure that can help to achieve compliance.

## Slide 34
Control of fugitive discharges: staff training, good housekeeping and storage practices, spill prevention and clean-up, and appropriate disposal and waste management
Process modifications: recycling, controlled release of batch discharges, and product substitutions
Pretreatment: segregation of streams and end of pipe treatment
Categories and examples of BMPs

## Slide 35: BMP Development and Implementation
Identify users/sources of pollutant discharges
Focus group meetings to develop BMP strategies
Determine achievable reduction
Develop BMP plans
Develop monitoring plan
Implement BMP and monitoring plan by Summer, 2005

## Slide 36: Comments on Use Of EPA Local Limits Development Guidance
Q&A – Can best management practices limits be applied in lieu of the traditionally derived numeric local limits?
  The current regulatory language is ambiguous as to whether BMP’s could serve in lieu of numeric limits.
  If adopted, the proposed Pretreatment Streamlining Rule would specify that BMP’s could be considered as local limits and so fulfill the statutory requirements of Section 307 (d) of the Clean Water Act.

## Slide 37: Comments on Use Of EPA Local Limits Development Guidance
Public Participation (6.8)
  Clarifies need for public notices, hearings, documentation, and approval of local limits.
  Phoenix strategy
    Early communication with EPA Region and State authority
    Special meetings for stakeholders – industries, environmental groups, regulators
    Developed local limits web site for document review (in addition to public libraries), comments, feedback
    English and Spanish language newspaper notification
    Formal public meeting had good participation, only minor comments
    Approval by regulatory agencies anticipated in near future

## Slide 38: Questions? THANKS!