## Slide 1: WET WEATHER MANAGEMENT PLAN Department of Public Utilities Division of Sewerage & Drainage Dax J. Blake, P.E., DOSD Assistant Administrator Michael B. Coleman, Mayor Cheryl Roberto, Director

## Slide 2: Background
July 1, 2005 – The City submitted our Wet Weather Management Plan to Ohio EPA
Related to two agreements signed by Columbus and the State of Ohio to reduce sewer overflows:
Sanitary Sewer Overflows (SSOs) - 2002
Combined Sewer Overflows (CSOs) - 2004
      Specific requirements must be met

## Slide 3: What Is The Wet Weather Management Plan (WWMP)?
Capital Improvement Plan for Columbus’ sewer system and treatment plant improvements
System Characterization for collection system and receiving streams
System Evaluation and Capacity Assurance Plan (SECAP) for separate sanitary sewers
Long Term Control Plan (LTCP) for combined sewers
No Feasible Alternative (NFA) analysis done at both wastewater treatment plants (Jackson Pike and Southerly)

## Slide 4: In other words…
The WWMP is an integrated plan to address
The selected level of control (LOC) for CSOs
The selected level of service (LOS) for SSOs
The selected LOS for treatment plant bypasses
The challenge was taking a system that is integrated today and providing for different standards of capture and treatment.

## Slide 5: The SECAP
Primarily addresses LOS for SSOs and treatment plant bypasses
Used a flow-based analysis of collection system flow meter data to estimate a level of service
Relies primarily upon tunnels for conveyance and storage as well as treatment plant improvements
Current plans for about 25 miles of 14-foot diameter tunnels and one 250 mgd pump station

## Slide 6: SECAP LOS Selection
Macro level model to look at over 12,000 possible combinations of tunnel and treatment sizes
  The knee of curve was near 1-year LOS
10-year LOS selected for the collection system
1.4 year LOS selected for the treatment plant bypasses
Selection based on non-monetary factors
The plan DOES NOT include blending

## Slide 7: The LTCP
Included an evaluation of presumptive measures and demonstration measures
  Consent order essentially required both
Used a typical year of rainfall to analyze the response of the collection system
  Collection system model linked to WASP6 water quality model and bacteria spreadsheet model
Much of the plan development revolved around presumptive measures – primarily frequency

## Slide 8: LTCP LOC Selection
Recommended alternative selected based on non-monetary and cost factors
  Lowest cost (at the selected LOC) and highest benefit in non-monetary factors
LOC selection driven by sensitive areas criterion
  Primary Contact Use designation – all receiving streams
  Distinguished areas by surrounding land use
Treatment plant improvements – common to SECAP and LTCP
  Presents challenges for operation strategy

## Slide 9: LTCP LOC Selection
Recommended plan consolidated lower half of CSOs into a common pipe with one overflow (14-foot diameter)
Upper half of combined system addressed with storage tanks
High rate treatment system proposed at downstream end of the system – 250 mgd
All CSOs either consolidated or controlled to 1-year LOC
CSO HRT capacity exceeded and overflows at a 3-month LOC

## Slide 10: No Feasible Alternative - WWTPs
Comprehensive evaluation of hydraulics and processes
  Hydraulic model, Process Model, CFD Model
Squeezes as much flow through the plants as possible
Modifies/expands processes to maintain compliance with NPDES permit limits (7-day Average) with 50% increase in throughput
Bypass analysis done as part of SECAP
  Differing tunnel sizes with treatment plant capacities

## Slide 11: Schedule for Implementation
CSO consent order required 20-year schedule for LTCP
SECAP consent order included no specific end date
Schedule based primarily on affordability analysis
  Included factors for accelerated schedule
Selected a 40-year schedule for implementation
Little benefit to shorter schedule
  85% of the reduction in first 20 years

## Slide 12: What Will The Plan Cost?
Tunnels & pump station | $1.5 billion
Combined sewer solutions | $0.5 billion
Priority Areas & other improvements | $0.2 billion
Treatment plant improvements | $0.3 billion
Total Wet Weather Program Estimate | $2.5 billion
Other capital improvement projects (e.g. sewer rehabilitation) over 40 years | $2.9 billion
TOTAL (in present day costs) 40 yrs. | $5.4 billion

## Slide 13: Overflow Reduction Over Time

## Slide 14: Environmental Benefits 30 vs. 40 Year Schedule

## Slide 15: WWMP Submitted in Two Parts
Interim Plan – Addresses specific CSO consent order requirement
  A “substantial reduction” in our single largest CSO
  Interim plan achieves a 70% reduction at this CSO
  2-miles of 14-foot sewer and 50% increase in biological treatment capacity at WWTPs
WWMP – Addresses LTCP, SECAP, and NFA over 40-year timeframe

## Slide 16: Plan Approval
Interim Plan approved April 28, 2006
Currently discussing the entire WWMP with OEPA
  Reviewing content of WWMP to assist understanding – (six-foot tall document)
  Concerns with WWTP Bypass LOS
  Concerns with collection system modeling
  Concerns with Affordability Analysis and associated schedule

## Slide 17: Questions?

## Slide 20: How To Review The Plan
Appointments can be made at 910 Dublin Rd. or Fairwood Ave.
Copy of the 22-binder plan at the Columbus main library
Disk sets available for purchase for $2 at the 910 Dublin Rd. Permit Office

## Slide 21: Current Wet Weather Problems
Typical year CSO discharge = 1.25 billion gallons
Average annual SSO discharge = .35 billion gallons (as often as once per month)
Historical annual Southerly plant bypasses ≈ 10
2004 reported basement backups = 508
With no action, these problems would only get worse

## Slide 22: Stream Quality Study
Extensive stream study done
Samples collected from: Scioto and Olentangy Rivers; Big Walnut, Alum and Blacklick Creeks
Results indicated that streams met chemical water quality standards
Results indicated that streams did not meet bacterial water quality standards during wet weather
Several species not seen in more than a decade were found
This section available on Division of Sewerage and Drainage web site at www.sewers.columbus.gov

## Slide 23: CSO LOCATIONS
Jackson Pike WWTP
Southerly WWTP

## Slide 24: SSO LOCATIONS
Jackson Pike WWTP
Southerly WWTP

## Slide 25
Reported Basement Backup Locations
Not all basement backups are capacity related
Jackson Pike WWTP
Southerly WWTP

## Slide 26: Interim CSO Control Plan
New sewer to be built from Whittier Street Storm Tank (where majority of CSOs occur) to Jackson Pike Wastewater Treatment Plant
  in design and to be completed by 2010
CSO regulator adjustments (weir raises)
Increase wet weather capacity at Jackson Pike by approximately 50 million gallons per day
Increase wet weather capacity at Southerly by approximately 105 million gallons per day

## Slide 27: New sewer from Whittier to Jackson Pike (“OARS” - OSIS Augmentation Relief Sewer, Phase 1)

## Slide 28: Benefits Of Interim Plan
Reduction of typical year CSO volume at Whittier St. overflow from 1 billion gallons to 312 million gallons (70% reduction)
CSOs from Whittier Street relocated to Jackson Pike
Reduction of typical year CSO volume at all CSOs by 67%

## Slide 29: Overall Plan Includes Four Types of Improvements 1. SSOs—Large Scale System Strategies -Two Tunnels (Olentangy & Alum Creek) -Olentangy Pump Station 2. SSOs—Small Scale - 12 Priority Areas 3. CSOs - New Whittier- Jackson Pike Sewer 4. Treatment Plants

## Slide 30: Wet Weather Management Plan Benefits
Estimated 1.4 billion gallons of annual overflow reduction after plan completed
Over 85% of the average annual reduction occurs in the first 20 years
Improved level of service along main trunk sewers
  Now: Some overflow as much as once per month
  Future: Overflows no more than once every 10 years

## Slide 31: Benefits continued
An improved Priority Area SSO level of service of 5 to 25 years, depending on area
Significant reduction of sewer backups
  Project Dry Basement backflow prevention program is scheduled to continue
An improved combined sewer level of control
  Zero overflows except at the Jackson Pike high rate treatment facility in a typical year
  Only four untreated overflows at Jackson Pike high rate treatment facility

## Slide 32: Benefits continued
Increased capacity at the wastewater treatment plants
  Bypasses from 10 or more times per year to once every 1.4 years at Southerly
  Zero bypasses expected at Jackson Pike
  Increased biological treatment capacity from 325 to 600 million gallons per day

## Slide 33: Improvements Schedule
Assumes Jan. 1, 2006 plan approval from OEPA
City selected 40-year schedule to spread out the construction and debt payment for affordability
Alum Creek Relief Tunnel design to begin 2005 with construction anticipated to begin in 2011
Olentangy Relief Tunnel design to begin 2014 with construction anticipated to begin in 2025

## Slide 34: Improvements Schedule
CSO Consent Order projects
  Interim date of 2010 to be met
  Remainder of projects as quickly as practical; all projects completed by 2025
SSO Consent Order projects
  No end date required
  City used affordability analysis and community’s ability to pay to set schedule

## Slide 35
Affordability Analysis Purpose
To ensure that any schedule for improvements is as expeditious as possible while maintaining affordable rates
for all consumers

## Slide 36: Affordability Analysis
Was done to determine residents’ ability to pay for the improvements
  Unless federal funding becomes available, rate payers will finance the plan
City examined 20, 30 and 40-year schedules
EPA provides affordability guidelines that can be used but City of Columbus looked beyond those
Other information considered
Schedule compression costs
Cost benefit analysis of schedules

## Slide 37: Affordability Analysis continued
Analysis is based on long-term projections
  Costs estimates, population growth estimates
We need to continually measure affordability
City and Sewer and Water Advisory Board developed “Measures of Success”
  Schedule may be adjusted if needed to meet Measures of Success

## Slide 38: Measures Of Success
Major Category | Components
Overall Effects | Maximum aggregate bill increase % of customers in Steps 3 & 4 Delinquency
Vulnerable Populations Effects | Maximum % household income for vulnerable population segment
Local Economy/ Business Health Effects | Housing starts Employment
Housing Effects | # households mortgage eligibility affected # of renters driven over housing cost burden threshold

## Slide 39: What Should Ratepayers Expect?
Sanitary sewer rates could reach as high as 2.6 times current rates (average quarterly bill currently is $72)
  This increase will not apply to water or stormwater fees
Rates will be reviewed each year
Trigger mechanisms are built into the review
  Schedule lengthened if triggers are activated
  Schedule accelerated if outside funding received

## Slide 40: Economic Benefits Expected
According to the Columbus Chamber of Commerce, we can expect $12.5 billion in economic benefits for our area from the plan over the 40 years:
  An average of 1,281 construction jobs annually
  An average of 2,897 total jobs annually
  Generating $4.5 billion in payroll
  And $76.4 million in tax receipts

## Slide 41: Ways Residents Can Lower Their Sewer Bills
Water conservation – bills are based on water consumption. Examples: wash dishes and laundry only on full loads, fix leaks, use low-flow fixtures and water lawns and plants only when needed
Senior Citizen Discounts are available to income-eligible residents over 60 - call 645-8270
Auxiliary meters are available for high consumption of water that does not enter the sanitary system (i.e. filling pools) – call 645-8164

## Slide 42: Next Steps
Comments on the plan due November 1, 2005
  Public can submit comments to DOSD
City awaits approval of the plan from Ohio EPA, while proceeding with improvements already underway
After projects are designed, additional public meetings will be held before construction

## Slide 43: Summary
Estimated 1.4 billion gallons of annual overflow reduction, a vast majority of which is achieved early in the program
Improved level of service – reduced sewer backups, SSOs and CSOs
Addressing the problems in our sewer system will make central Ohio a cleaner and healthier place to live, work and play