## Slide 1: Selecting and Living with CSO Performance Measures The Wet Weather Partnership and National Association of Clean Water Agencies June 2, 2006
Ralph M. Wallace
Massachusetts Water Resources Authority

## Slide 2: MWRA Sewer System
Wholesale provider of water and sewer services
2.5 million served
Deer Island Treatment Plant - 1,270 mgd capacity
43 sewer system communities
4 communities have CSOs - Boston, Cambridge, Chelsea and Somerville

## Slide 3: MWRA CSO Program – Key Dates
1987 MWRA assumed responsibility for developing and implementing a regional long-term CSO control plan
1994 Conceptual Plan formed basis for Federal Court schedule
1997 Facilities Plan/EIR established long-term level of control for most receiving waters with variances issued for the
  Charles River, Alewife Brook and Upper Mystic River.
2006 Court Order revisions established long-term plan and level of control for all receiving waters through 2020;
require three-year performance assessment

## Slide 4: Goals of MWRA’s Long-Term Control Plan
95% capture to secondary treatment
Eliminate CSO discharges to sensitive use areas (maintain Class B)
Close 36 of 84 outfalls
Reduce CSO discharges to meet Bcso standard (>95% compliance with Class B) in less sensitive areas
Treat CSO discharges where significant contribution
Reduce annual overflow volume from 3.3 BG in 1988 to 0.5 BG with 94% of remaining overflow receiving fine screening, disinfection and dechlorination
Control floatables in all remaining discharges

## Slide 5: CSO Performance Measures - Developed from Bcso Water Quality Standard
Comply with national use standards at least 95% of time.
Approved facilities plan justifies level of control >95% compliance as most environmentally protective and cost-effective
UAA based on facilities plan finds that higher level of CSO control is not feasible or appropriate
Existing uses and the water quality to protect these uses are maintained
Performance Standards Driven by Water Quality and Use Protection

## Slide 6: Establishing CSO Performance
Collection system hydraulic modeling to predict CSO discharge performance
Annual simulations using a typical rainfall year (based on 40 years of rainfall records, and approved by EPA and Mass. DEP)
Receiving water quality modeling to predict cumulative annual duration of exceedances

## Slide 7: Establishing CSO Performance
Model predicted performance of recommended plan at each outfall drove numerical goals
  Activation frequency
  Total annual discharge volume
  % compliance with National Use Standards in receiving water segment
Performance goals drove NPDES permit limits
  Activation frequency at every outfall
  Total annual discharge volume at every outfall
  CSO treatment facility discharges must additionally meet water quality limits at all times

## Slide 8: Measuring and Tracking CSO Performance
NPDES annual CSO discharge estimating and reporting
  All outfalls and all storms in previous year
  Modeling supported/verified with limited monitoring
  # of activations, discharge volume and duration
  Comparison to expected current conditions
  Comparison to CSO control goals, accounting for actual rainfall and status of LTCP implementation
Court-ordered three-year performance assessment at end of LTCP implementation

## Slide 9: Detailed InfoWorks Hydraulic Model
Over 100 Miles of Community Sewers
230 Miles of MWRA Interceptors
5 Pump Stations
4 Headworks
181 Regulators
138 Tidegates
1800 Connections
700 Drainage Subareas
3200 Conduits
3000 Nodes

## Slide 10: Water Quality and Technology Evaluations Led to Outfall Specific Levels of Control – Alewife Brook

## Slide 11: Annual Performance Monitoring
Update model configuration (new system information, completed projects)
Model set-up
  Rainfall
  Tide
  Headworks flow data
  CSO facilities
  Snowmelt
Analyze rainfall data and compare to typical year
Check model calibration using permanent and temporary meters
Compare annual estimates (model predictions or CSO facility data) to LTCP goals
Conduct follow-up where results differ from expectations

## Slide 12: Hydraulic Model Accuracy – NPDES Report for 2005
Outfall | Overflow Meters |  | Model Results |  |  | 
 |  |  | w/o Sediment |  | w/ 18" Sediment in SBI between BOS082 and BOS083 | 
 | Activation Frequency | Volume (MG) | Activation Frequency | Volume (MG) | Activation Frequency | Volume (MG)
BOS081 | 7 | 0.17 | 4 | 0.24 | 7 | 1.16
BOS082 | 7 | 1.78 | 2 | 0.29 | 8 | 1.43
BOS083 | 0 | 0 | 2 | 0.12 | 2 | 0.08
BOS084 | 4 | 0.09 | 2 | 0.12 | 2 | 0.10
BOS085 | 0 | 0 | 0 | 0 | 0 | 0
BOS086 | 1 | 0.52 | 2 | 0.25 | 2 | 0.25

## Slide 13: MWRA’s CSO Performance Measures - Disadvantages
Outfall specific performance standards limit flexibility and increase monitoring and reporting requirements – consider receiving water based standards.
Outfall specific performance standards can increase the number of site-specific violation claims.
Models are costly to develop and require ongoing maintenance and calibration.
Compliance with numerical discharge (as opposed to receiving WQ) limits can lead to higher plan costs.

## Slide 14: MWRA’s CSO Performance Measures - Advantages
Long-term federal and state regulatory agreement on levels of control and recommended plan provide assurance of financial impact control.
Quantitative and specific performance measures can limit regulatory and third party interpretation and provide a clear basis for defense from violation claims.
Typical year performance limits provide relief from violations for extreme wet weather events when flood control is the priority.
Long-term federal and state regulatory agreement on levels of control and recommended plan moves plan implementation and water quality benefits forward.
Job security for wastewater modeler.

## Slide 15: CSO Construction Progress

## Slide 17: Cottage Farm Annual Discharges Reduction
1,547
117.1
24.0
6.3
0
200
400
600
800
1,000
1,200
1,400
1,600
1,800
1988 Conditions
Existing Conditions
Recommended Plan
(January 2004)
Revised Recommended
Plan (June 2005)
18
16
6
2
0
2
4
6
8
10
12
14
16
18
20
1988 Conditions
Existing Conditions
Recommended Plan
(January 2004)
Revised Recommended
Plan (June 2005)
Number of Activations
Annual Volume (million gallons)

## Slide 18: Boston Harbor Average Enterococcus Counts in Wet Weather 1987-1991
Notes: Average wet weather bacterial water quality in Boston Harbor (some samples higher, some lower)
Monitoring data collected by MWRA’s Central Lab and Environmental Quality monitoring program in Boston Harbor and tributary rivers, and from MDC’s beach monitoring.
Enterococcus is the sewage indicator bacteria recommended by EPA for monitoring marine waters.
Contours show the geometric means of Enterococcus data collected when more than 0.2 inches of rain had fallen in the previous 24 hours;
blue areas meet the EPA standard and red-purple areas exceeded the standard.
1987-1991 shows data from before the Boston Harbor project and CSO plans began up through the last year that sludge was discharged (1991).
In wet weather most of the Inner Harbor, the tributary rivers, failed the standard, some with extremely high counts
areas affected by discharges of sewage and sludge from the DITP and NITP failed the standard

## Slide 19: Boston Harbor Average Enterococcus Counts in Wet Weather 1999-2005
1999-2005
Notes: 1999-2003
shows continued improvement due to closure of 22 CSO outfalls,
upgrades of CSO facilities,
ending of harbor treatment plant effluent discharges as the new 9.5 mile outfall began operating in September 2000,
and local efforts to abate stormwater pollution.
Dramatic improvements to Harbor have brought back boaters, swimmers, fishermen and proved a boon for tourism and waterfront development.

## Slide 20: Further Information
Contact Ralph Wallace
  Telephone - (617) 788-4917
  e-mail - ralph.wallace@mwra.state.ma.us
www.MWRA.com
  News – “MWRA Reaches Landmark Agreement Over Long-Term CSO Control Plan” 3/16/06
  Reports – Annual CSO Control Plan Progress Report