## Slide 1
Aoccdrnig to rscheearch at an Elingsh uinervtisy, it deosn't mttaer in waht oredr the ltteers in a wrod are, the olny iprmoetnt tihng is taht the frist and lsat ltteer are in the rghit pclae. The rset can be a toatl mses and you can sitll raed it wouthit a porbelm. Tihs is bcuseae we do not raed ervey lteter by it slef but the wrod as a wlohe and the biran fguiers it out aynawy.
Our Amazing Brains…

## Slide 2: 50 POTW Study Update

## Slide 3: 50 POTW Study
Original Study Data from Late 1970’s
  “Fate of Priority Pollutants in Publicly Owned Treatment Works”, September 1982
  POTWs in study were not named in document
Used in Effluent Guidelines Development
Published as “Literature Values” in EPA Local Limits Guidance

## Slide 4: Effluent Guidelines Development
EPA determines pollutant pass through by comparing the percentage removed by POTWs with the percentage removed by direct dischargers using BPT/BAT technology.

## Slide 5: Effluent Guidelines Development
A pollutant “passes through” POTWs when the average percentage removed by well-operated POTWs nationwide (those meeting secondary treatment requirements) is less than the percentage removed by direct dischargers complying with BPT/BAT limitations for a given pollutant.

## Slide 6: Local Limits Development
Used in Local Limits Calculations for Allowable Headworks Loadings [AHL]
  Removal Rates
    Used in “NPDES Pass-Through” Calculations
  Inhibition Values
    Used in Interference Calculations
    Activated Sludge/Nitrification/Trickling Filter
  Determining Pollutants of Concern

## Slide 7: Original 50 POTW Study
Pollutants
  “Routine” Metals
  Cyanide
  A few organic priority pollutants
Types of POTWs
  Activated Sludge
  Activated Sludge with nitrification
  Trickling Filters
  “Tertiary” Treatment

## Slide 8: Why Update The 50 POTW Study?

## Slide 9
1977-1978
ELVIS LEFT THE BUILDING
Notes: Ah 1977 and 1978…..
John Travolta….for you environmental youngsters out there…Saturday Night Fever showed John Travolta could dance long before he took the floor in Pulp Fiction. The movie and the soundtrack were both blockbusters….
President Carter negotiated the Camp David Peace Accord between Israel and Egypt….
We discovered that the Love Canal had nothing whatsoever to do with romance
The first test tube baby proved we didn’t need romance to make a baby
And most people think that Elvis Left the Building for the last time….
[Playing “Stayin’ Alive” by Bee Gees]

## Slide 10: Why Update the Study?
Data is over 25 years old
Advances in POTW treatment technologies
  Study data no longer reflect current POTW performance
Advances in Laboratory/Wastewater Analysis technology
  Clean sampling/Low Level Metals analysis

## Slide 11: Why Should We Care?
Some States Require POTWs to Use EPA Literature Values in certain cases
  If no site-specific data is available
  If more than 50% of site-specific data for a particular pollutant is BDL
  If POTW chooses to use EPA literature values [may be problematic]

## Slide 12: For Instance:
Greensboro, North Carolina
  Using “old” mercury method with 200 ppt [0.2 ug/l] detection limit
    Virtually all POTW inf/eff data was BDL
    Forced to Use EPA Median Mercury RR of 67%
  Using EPA 1631 Low Level Mercury method with 1 ppt [0.001 ug/l] detection limit
    Mercury Removal Rates dramatically higher
    Combination of better analytical methods AND upgraded POTW

## Slide 13: POTW #1 Design Flow 16 MGD NPDES Mercury Limit: 12 ng/l (ppt) “Pass-Through Calculation”
Removal Rate Source | INF ng/l | Eff ng/l | % REM | MAHL (in lbs)
Method 245.1 | <200 | <200 | n/a | n/a
50 POTW Study | n/a | n/a | 67 | 0.0045
Method 1631** | 265 | 5.8 | 97.8 | 0.0728
**145 Data Sets of Influent and Effluent Samples

## Slide 14: POTW #2 Design Flow 40 MGD NPDES Mercury Limit: 12 ng/l (ppt) “Pass-Through Calculation”
Removal Rate Source | INF ng/l | Eff ng/l | % REM | MAHL (in lbs)
Method 245.1 | <200 | <200 | n/a | n/a
50 POTW Study | n/a | n/a | 67 | 0.012
Method 1631** | 51.1 | 5.9 | 88.4 | 0.0345
**147 Data Sets of Influent and Effluent Samples

## Slide 15: Importance of RR Values
Same POTW: 0.002 mg/l NPDES Cadmium Limit
5.0 MGD Flow
RR | MAHL [lbs]
46.0% | 0.154
56.0% | 0.190
66.0% | 0.245
76.0% | 0.348
RR | MAHL [lbs]
86.0% | 0.596
96.0% | 2.085
98.0% | 4.170
98.5% | 5.560
NPDES “Pass-Through” Calculation
Notes: We’ve seen how important removal rates are for BOD, now lets’ take a quick look at an example of how important removal rates are for metals, too.
The chart above includes removal rates with differences of up to 10%. As you can see there is not much difference until you get up to the 76% value, but look at the difference between 86% and 96%. And then, examine the difference between 96.0% removal and 98.0% removal. Now, how about between 98.0% and 98.5%? Wow!
So, as we look at the various ways to calculate removal efficiencies just keep in mind how much the Maximum Allowable Headworks Loading may change with just a small difference in the % removal efficiency, especially in the high 90 percent range.
Here we have our same POTW that just happens to be on a very, very small stream so their NPDES permit limit for cadmium is 0.002 mg/l or 2 ppb….
Let’s look at the removal rates with differences of 10% in the chart. As you can see there’s not a whole lot of difference until you get up to the 76% value, but look at the difference between 86% and 96%……Wow….
So as we look at the various ways to calculate removal efficiencies just keep in mind how much the MAHL may change with just a small difference in the % removal especially in the high 90 percent range….

## Slide 16: What Does NACWA Want to Do?
“Mine” existing POTW data that has been submitted to EPA/States
Review existing data and determine any “data gaps”
Plan additional data collection for any gaps

## Slide 17: What Do We Need?
Pollutants
  Metals [“Routine” and Weird Ones]
  Conventional pollutants [BOD/TSS/NH3H/ TP]
  Emerging pollutants [Pharmaceuticals, Personal Care Products, etc.]
Types of POTWs???
  Secondary treatment, “Advanced” secondary treatment, Biological Nutrient Removal, various biological processes

## Slide 18: Potential Stumbling Blocks
EPA Acceptance of “Mined” Data
  DMR Data
    Routinely submitted for compliance purposes
  Criteria to Select POTWs
Funding for Data Analysis
  “Mined” by NACWA….Analysis/Statistics by Contractor?
Data Decisions
  How many samples…how many POTWs?
  How to handle BDL data

## Slide 19: What Might We Need?
YOUR Time and YOUR Headworks Analysis Data
  POTW Influent and Effluent values to calculate removal efficiencies
  Biological process data [e.g. activated sludge, trickling filter] to determine inhibition levels [or lack of inhibition!]
  Information about your POTW and Influent Characteristics

## Slide 20: What Do We Need Now?
Survey Response Today
Your Opinion
  How Important is this to YOU and YOUR program?
  Would your program use the updated data?

## Slide 21: QUESTIONS?
How many of you used EPA Literature Values in determining/calculating any one of YOUR local limits?
  Removal rates or inhibition values
Did you use them by “choice or force”?
What State Are You From?